| No. | Purchaser Comment | Vendor Reply | Conclusion |
| --- | --- | --- | --- |
| G - General |  |  |  |
|  | VENDOR is sole responsible to consider this clarification and modify his offer based on this TCL. All modifications considered on the next revision of offer based on this clarification should be clearly marked with revision and cloud marks. All consequences due to changes without cloud mark are in VENDOR’s responsibilities. Anyway, this clarification has priority over the offer. | Confirm |  |
|  | Vendor to confirm that scope of work and supply are in full compliance with Material Requisition (MR) and its attachments and relevant codes and standards mentioned on MR and specifications. Vendor shall mention any deviation / alternative compared with requirements of MR and its attachments on the Bidder’s signed/ stamped Deviation Form (Attachment #5 of MR) with sufficient technical reasons. Purchaser has no responsibility to discover any deviations entered in Vendor’s proposal. Deviations which are not listed in the Deviation Form are not valid and in case of order no deviation or alternative would be acceptable except the ones specified on the mentioned form and finalized before order at clarification stage. General Statement that “Other Parts not expressly specified in our quotation is not in our scope of work / supply will not be acceptable since any deviation with respect to MR should be clearly specified. * Only Deviation lists with Bidder’s signature / Stamp would be acceptable. | Confirm |  |
|  | Packing, shipping preparation and preservation should be done according to approved procedure considering all requirements on MR and its attachments. | Confirm |  |
|  | In case of order, all drawings and calculation books should be issued along with relevant native file | Confirm |  |
|  | Regarding Sub-VENDORs/sub-suppliers, VENDOR shall note that PURCHASER have the right to reject sub-VENDORs/sub-suppliers if his capability is judged poor or not proven. | Confirm |  |
|  | VENDOR shall confirm that technical documentation, No. of copies and the submission time will be according to the relevant attachment of Requisition (#1). In addition to PDF format, Auto-CAD files for all drawings shall also be submitted. | Confirm |  |
|  | Surface preparation and Painting should be performed based on relevant specifications. Primer, intermediate and final coat should be carried out based on approved painting procedure in VENDOR’s shop before shipment. | Confirm |  |
|  | Generally, vendor should confirm all materials would be in full compliance with relevant specifications and Engineering drawing attached to MR (Material Requisition). Unless exceptions, deviations or alternatives are clearly identified on Deviation list attached to MR. | Confirm |  |
|  | Vendor shall note that the Guarantee time to be a period of 12 months after successful start-up or 18 months after shipping whichever comes earlier. | Confirm |  |
|  | A complete catalog of all suggested products shall be attached to the revised offer. | Confirm |  |
|  | The following documents shall be furnished and submitted after PO as minimum: - General arrangement - Single Line Diagram - Schematic and Wiring Diagram - Data Sheet | Confirm |  |
| T - Technical |  |  |  |
|  | Type test certificates (for IP) shall be submitted. | Confirm |  |
|  | Preliminary ITP shall be submitted. | Confirm |  |
|  | Only the major component specification has been reviewed in submitted proposal. As vendor submitted his proposed part list, please note that vendor is sole responsible for any discrepancy between provided quantity in submitted offer and required quantity based on ADISH submitted SLD. | Confirm |  |
|  | Country of origin shall be specified in sub vendor list. | Confirm |  |
|  | Painting procedure shall be as below: For outdoor panels, painting coating thickness must be 270 microns as minimum. 3-layers based on the approved painting procedure shall be provided. For indoor panels, one-layer powder painting is accepted based on the approved painting procedure. | All panels are coated with 80~120 µ thickness electrostatic powder paint. Galvanized sheet is used for Outdoor panels. |  |
|  | MCB for lighting purposes shall be type "B". | Confirm |  |
|  | All equipment (Busbar, CB, …) shall be de-rated for project site condition by vendor. Please be noted: - Max. Design Ambient temperature for indoor panels shall be +40ºC. - Max. Design Ambient temperature for outdoor panels shall be +48ºC. - Site Altitude (a.s.l): Less than 150 - Seismic Condition: 3g - Design humidity: 80% (De-rating factors must be calculated and implemented). | Confirm |  |
|  | - Indoor panel shall be min. IP41 - Outdoor panel shall be min. IP55 - Outdoor panel (IP55) shall be equipped via sun shade. | Confirm |  |
|  | - All bus bars shall be heat shrink and color marked. - Busbar joint shall be tin coated. | Confirm |  |
|  | The ventilation type for all panels shall be air-natural. | Confirm |  |
|  | - Commissioning spare part list is not an option and vendor shall be proposed and to be considered it in your price. - 2-year spare part list shall be offered as option. | Confirm |  |
|  | Earth lug on the frame and enclosure of the panel shall be considered. | Confirm |  |
|  | For UPD panel, battery pack and UPS system is out of vendor scope of supply and only distribution shall be supplied. Incoming CB for UDP-S75-001 shall be MCCB 4P 25A. | Confirm |  |
|  | Wooden packing shall be provided by vendor for all panels. | The request was deleted. |  |
|  | 20% Space shall be provided for all panels. | Confirm |  |
|  | Contactor type feeders in all submitted SLDs shall be equipped via on/off signal lamp. | Confirm |  |
|  | All outdoor panels shall be equipped via thermostat. | Confirm |  |
|  | For all incoming panels all power loss signal shall be provided for all incomings. | Confirm |  |
|  | One common fault shall be provided for sending to remote system (consist of all CBs’ faults). | Confirm |  |
|  | Incoming feeder of panel HVP-S75-001 has interlock (shutdown/trip) with F&G system. | Confirm |  |
|  | RAL color for Heat Trace Panels is RAL7040 and others are RAL 7035. | Confirm |  |
|  | SHEET THICKNESS for wall mounted panel shall be min. 1.5mm and 2mm for semi standing panels. | Confirm |  |
|  | Gland plate shall be provided by vendor. Drilling data will be finalized and sent to vendor after bidder selection at detail design stage (without cost and time impact). | Confirm |  |
|  | For all panels same dimension has been specified. Please be noted in case of change in dimension, all adjacent panels shall be designed and fabricated in the same frame size. | Confirm |  |
|  | For other comments please refer to attached file. | Confirm |  |