## TW-521-210AB
Thermowell
|  | Tag No. |  |  | Qty | TW-521-210A/B |  |  | 2
Thermowell | 43 | Process Connection | Size | Rating | Facing | 1 1/2" | #600 |  | R.F
| 44 | Connection Type |  |  |  | Tapered drilled bar stock with full penetration welding
| 45 | Well & Flange Material |  |  |  | SS316/316L
| 46 | Instrument Connection |  |  |  | 1/2" NPTF
| 47 | Insertion Length (U) mm |  |  |  | 200mm
| 48 | Lagging Extension (T) mm |  |  |  | 75mm
| 49 | Bore Diameter | Tip Thickness |  |  | 6.6mm |  | 6.4mm
| 50 | Root Diameter | Tip Diameter |  |  | 36mm |  | 30mm
| 51 | Treatment | Coating |  |  | - |  | -
| 52 | Finish |  |  |  | -
| 53 | Stamping |  |  |  | -
| 54 | Name Plate Material |  |  |  | Stainless Steel
| 55 | Standard Drawing Number |  |  |  | -
| 56 | Anti Abrasion Material | Anti Abrasion Thickness (mm) |  |  | - |  | -
| 57 | Screwed Plug and Chain |  |  |  | Yes (316SS)
| 58 | Wake Frequency Calculation |  |  |  | Required (ASME PTC 19.3TW-latest version)
Fluid Operating Data |  | Fluid |  |  |  | High Pressure Steam
|  | Flow (Kg/h) |  |  |  | 4525
|  | Pressure (barg) |  |  |  | 44.9
|  | Temperature (°C) |  |  |  | 350
|  | Max. Velocity (m/s) |  |  |  | 29.1
|  | Medium Density (Kg/m³) |  |  |  | 17.1
|  | Dynamic Viscosity (cP) |  |  |  | 0.022

## TW-521-211AB
Thermowell
|  | Tag No. |  |  | Qty | TW-521-211A/B |  |  | 2
Thermowell | 43 | Process Connection | Size | Rating | Facing | 1 1/2" | #300 |  | R.F
| 44 | Connection Type |  |  |  | Tapered drilled bar stock with full penetration welding
| 45 | Well & Flange Material |  |  |  | SS316/316L
| 46 | Instrument Connection |  |  |  | 1/2" NPT
| 47 | Insertion Length (U) mm |  |  |  | 200mm
| 48 | Lagging Extension (T) mm |  |  |  | 75mm
| 49 | Bore Diameter | Tip Thickness |  |  | 6.6mm |  | 6.4mm
| 50 | Root Diameter | Tip Diameter |  |  | 34mm |  | 30mm
| 51 | Treatment | Coating |  |  | - |  | -
| 52 | Finish |  |  |  | -
| 53 | Stamping |  |  |  | -
| 54 | Name Plate Material |  |  |  | Stainless Steel
| 55 | Standard Drawing Number |  |  |  | -
| 56 | Anti Abrasion Material | Anti Abrasion Thickness (mm) |  |  | - |  | -
| 57 | Screwed Plug and Chain |  |  |  | Yes (316SS)
| 58 | Wake Frequency Calculation |  |  |  | Required (ASME PTC 19.3TW-latest version)
Fluid Operating Data |  | Fluid |  |  |  | Medium Pressure Steam
|  | Flow (Kg/h) |  |  |  | 4525
|  | Pressure (barg) |  |  |  | 21.8
|  | Temperature (°C) |  |  |  | 310
|  | Max. Velocity (m/s) |  |  |  | 27.4
|  | Medium Density (Kg/m³) |  |  |  | 8.9
|  | Dynamic Viscosity (cP) |  |  |  | 0.02

## TW-521-218AB
Thermowell
|  | Tag No. |  |  | Qty | TW-521-218A/B |  |  | 2
Thermowell | 43 | Process Connection | Size | Rating | Facing | 1 1/2" | #600 |  | R.F
| 44 | Connection Type |  |  |  | Tapered drilled bar stock with full penetration welding
| 45 | Well & Flange Material |  |  |  | SS316/316L
| 46 | Instrument Connection |  |  |  | 1/2" NPT
| 47 | Insertion Length (U) mm |  |  |  | 200mm
| 48 | Lagging Extension (T) mm |  |  |  | 75mm
| 49 | Bore Diameter | Tip Thickness |  |  | 6.6mm |  | 6.4mm
| 50 | Root Diameter | Tip Diameter |  |  | 36mm |  | 30mm
| 51 | Treatment | Coating |  |  | - |  | -
| 52 | Finish |  |  |  | -
| 53 | Stamping |  |  |  | -
| 54 | Name Plate Material |  |  |  | Stainless Steel
| 55 | Standard Drawing Number |  |  |  | -
| 56 | Anti Abrasion Material | Anti Abrasion Thickness (mm) |  |  | - |  | -
| 57 | Screwed Plug and Chain |  |  |  | Yes (316SS)
| 58 | Wake Frequency Calculation |  |  |  | Required (ASME PTC 19.3TW-latest version)
Fluid Operating Data |  | Fluid |  |  |  | High Pressure Steam
|  | Flow (Kg/h) |  |  |  | 4525
|  | Pressure (barg) |  |  |  | 44.9
|  | Temperature (°C) |  |  |  | 350
|  | Max. Velocity (m/s) |  |  |  | 29.1
|  | Medium Density (Kg/m³) |  |  |  | 17.1
|  | Dynamic Viscosity (cP) |  |  |  | 0.022

## TW-521-170
Thermowell
|  | Tag No. |  |  | Qty | TW-521-170 |  |  | 1
Thermowell | 43 | Process Connection | Size | Rating | Facing | 1 1/2" | #600 |  | R.F
| 44 | Connection Type |  |  |  | Tapered drilled bar stock with full penetration welding
| 45 | Well & Flange Material |  |  |  | SS316/316L
| 46 | Instrument Connection |  |  |  | 1/2" NPT
| 47 | Insertion Length (U) mm |  |  |  | 200mm
| 48 | Lagging Extension (T) mm |  |  |  | 75mm
| 49 | Bore Diameter | Tip Thickness |  |  | 6.6mm |  | 6.4mm
| 50 | Root Diameter | Tip Diameter |  |  | 36mm |  | 30mm
| 51 | Treatment | Coating |  |  | - |  | -
| 52 | Finish |  |  |  | -
| 53 | Stamping |  |  |  | -
| 54 | Name Plate Material |  |  |  | Stainless Steel
| 55 | Standard Drawing Number |  |  |  | -
| 56 | Anti Abrasion Material | Anti Abrasion Thickness (mm) |  |  | - |  | -
| 57 | Screwed Plug and Chain |  |  |  | Yes (316SS)
| 58 | Wake Frequency Calculation |  |  |  | Required (ASME PTC 19.3TW-latest version)
Fluid Operating Data |  | Fluid |  |  |  | High Pressure Steam
|  | Flow (Kg/h) |  |  |  | 11012
|  | Pressure (barg) |  |  |  | 45
|  | Temperature (°C) |  |  |  | 350
|  | Max. Velocity (m/s) |  |  |  | 29.1
|  | Medium Density (Kg/m³) |  |  |  | 17.2
|  | Dynamic Viscosity (cP) |  |  |  | 0.022

## TW-521-171
Thermowell
|  | Tag No. |  |  | Qty | TW-521-171 |  |  | 1
Thermowell | 43 | Process Connection | Size | Rating | Facing | 1 1/2" | #300 |  | R.F
| 44 | Connection Type |  |  |  | Tapered drilled bar stock with full penetration welding
| 45 | Well & Flange Material |  |  |  | SS316/316L
| 46 | Instrument Connection |  |  |  | 1/2" NPT
| 47 | Insertion Length (U) mm |  |  |  | 250mm
| 48 | Lagging Extension (T) mm |  |  |  | 75mm
| 49 | Bore Diameter | Tip Thickness |  |  | 6.6mm |  | 6.4mm
| 50 | Root Diameter | Tip Diameter |  |  | 34mm |  | 30mm
| 51 | Treatment | Coating |  |  | - |  | -
| 52 | Finish |  |  |  | -
| 53 | Stamping |  |  |  | -
| 54 | Name Plate Material |  |  |  | Stainless Steel
| 55 | Standard Drawing Number |  |  |  | -
| 56 | Anti Abrasion Material | Anti Abrasion Thickness (mm) |  |  | - |  | -
| 57 | Screwed Plug and Chain |  |  |  | Yes (316SS)
| 58 | Wake Frequency Calculation |  |  |  | Required (ASME PTC 19.3TW-latest version)
Fluid Operating Data |  | Fluid |  |  |  | Medium Pressure Steam
|  | Flow (Kg/h) |  |  |  | 11012
|  | Pressure (barg) |  |  |  | 21.8
|  | Temperature (°C) |  |  |  | 310
|  | Max. Velocity (m/s) |  |  |  | 21.1
|  | Medium Density (Kg/m³) |  |  |  | 9.1
|  | Dynamic Viscosity (cP) |  |  |  | 0.02